- PNEUMATIC SWINGING DOOR LOCKS

  - Detention-type, pneumatic door locks for swing doors, with factory-assembled units including integral electrical and pneumatic work.

  - Medium/Maximum Security

    - Series/Manufacturer:

      - 10120AP/Southern Steel Company

  - Function

    - When electrical power is applied to the solenoid valve, the latchbolt shall retract.

    - When power is removed, the latchbolt shall extend when door is opened, allowing the door to be slam-locked.

    - When the door is slam-locked, the lock shall automatically deadlock.

    - Each lock shall have a key operated manual unlock feature.  A high security mogul key cylinder shall be used to operate this feature.

    - Rotating the key shall mechanically retract the latchbolt.  Removing the key shall extend the bolt, locking the door if closed, and allowing the door to be slam-locked if open.

    - When the door is slam-locked in the manual mode, the lock shall automatically deadlock even in the event of a total loss of air supply and/or electric power.

  - Mechanical Components

    - Lock shall operate when supplied with air between 40 PSIG minimum and 100 PSIG maximum.

    - Lock shall operate as a fail-secure slam-lock.

    - Lock body shall be made of steel or stainless steel.

    - Lock shall be factory plumbed with a quick connect air fitting.

    - Latchbolt shall be alloy steel, case hardened Rockwell C 60 to a depth of 0.030" and shall have a 7/8" throw minimum.

    - Lock shall have a mechanical roller-bolt deadlock actuator, and shall automatically deadlock when door is closed.

    - Lock shall be supplied with a mogul key cylinder as standard.

    - Lock shall be supplied with a security ring for installation in hollow metal frame by hollow metal manufacturer to protect mogul cylinder.

    - Cylinder extensions shall be provided for locks keyed 2 sides or keyed stop side.

  - Electrical Components

    - Solenoid valve shall be 1.5 watt, 24 VDC, continuous rated by valve manufacturer.

    - Lock shall be provided with a lock status switch to provide interlocking capabilities.

    - Lock shall be factory wired to a plug disconnect.

    - Lock status switch shall provide the following indications:

      - Locked/deadlocked indication

      - Unsecure indication